## Sheet1
Client
Date
Job No. & Equipment No.
*Data to Change from Example for Other Heaters
Information Obtained or Derived from Data Sheet, Drawings and ASME Sec. II Part D
*Tube Material | SA688TP304N | From Manufacturer's Data Sheet
*Total No. U-tubes | 1941 | From Manufacturer's Data Sheet
*OD, in. | 0.625 | From Manufacturer's Data Sheet
*Thickness, in. | 0.057 | From Manufacturer's Data Sheet
*Straight length, in. | 391 | From Manufacturer's Data Sheet
*Thermal conductivity, Btu/hr ft deg F | 10.4 | From ASME Code Sec. II Part D
Tube Unit surface, sq ft/ft | 0.1636 | From HEI Closed FWH Stds. P62
Surface/straight leg sq.ft | 5.3306 | (Str. lngth/12)(tube unit surf.)
*Steam inlet saturation temp., deg F | 411.3 | From Manufacturer's Data Sheet
*Drains outlet temp., deg F | 377.3 | From Manufacturer's Data Sheet
*Inlet feedwater temp., deg F | 367.3 | From Manufacturer's Data Sheet
*Outlet feedwater temp., deg F | 413.3 | From Manufacturer's Data Sheet
Temperature rise, deg F | 46 | Outlet - inlet temperature
Terminal Temp Diff, Deg F | -2 | From Manufacturer's Data Sheet
Drains Cooling Approach | 10 | Drains outlet - FW inlet temp
*Feeedwater flow, lb/hr | 4939829 | From Manufacturer's Data Sheet
Zone (All Data Taken from Manufacturer's Documents) |  | Desup | Condense | Subcool
*Total Effective Surface, sq. ft./ From Manufacturer's Data Sheet | 21018
*Surface in zone, sq. ft. From Data Sht. |  | 1979 | 16576 | 2463
No. Tubes in Zone From Data Sht. |  | 1941 | 1941 | 1941
Zone Lgth, ft From Manufacturers Drawings |  | 6.25 | 52.2 | 7.75
*LMTD, Deg F From Data Sht. |  | 213.9 | 16.3 | 21.4
Resistances, hr-sq ft deg F/Btu |  | From Manufacturer's Data Sheet
*Tube side fouling From Data Sht. |  | 0.00025 | 0.00025 | 0.00025
*Tube side film From Data Sht. |  | 0.000306 | 0.00031 | 0.000318
*Tube wall From Data Sht. | 0.083 | 0.000555 | 0.000555 | 0.000555
*Shell side film From Data Sht. |  | 0.009779 | 0.0004 | 0.000937
*Shell side fouling From Data Sht. |  | 0.0003 | 0 | 0.0003
Sums of resistances |  | 0.01119 | 0.001515 | 0.00236
Overall HT Coef, U, Btu/hr-sq ft deg F 1/sum of resistance |  | 89.3655 | 660.066 | 423.7288
Duty=UA(LMTD), total/zonal | 238290000 | 37835000 | 178155000 | 22300000
*FW Av Sp. Ht, Btu/lb, Calc. From Data Sht. | 1.0487 | Total duty/(FW flow x FW temp. rise)
Note: FW Av Sp. Ht. May be Different from Steam Table Value
Sleeve information
Material From Data Sht. | SA688TP304
Sleeve Thickness, in., | 0.028 | As Decided with Sleeving Contractor
*Thermal conductivity, Btu/hr ft deg F | 10.4 | From ASME Code Sec. II Part D
Effect of plugging
No. of Plugged tubes in DSH and DC | 100 | From Plug Map
No. of full lengths to be sleeved | 100 | Decided By Utility |  | 0
Plugged Surf, sq. ft. tube unit surf. X zone lngth x No. plugged |  | 102.25 | 853.992 | 126.79
Duty decrease, Btu/hr U x plugged surf. x LMTD |  | 1954537.5335 | 9188164.7525 | 1149705.9322
Total duty reduction, Btu/hr | 12292408.2182 | Sum of plugged zonal surfaces
FW out temp decrease, deg F | 2.373 | Total duty reduction/FW flow
FW out temp with 100 plugged tubes, deg F, | 410.927 | Original out temp. - FW out temp decrease
TTD with 100 plugged tubes, deg F | 0.37295 | Steam inlet temp. - plugged tube out temp.
DCA with 100 plugged tubes, deg F | 10.5156 | DCA + (FW temp. rise x duty decrease/duty)
Effect of sleeving recovery of plugged tubes
Additional resistances in sleeved tubes, hr-sq ft deg F/Btu
*Sleeve metal | 0.00027263
*Contact resistance, hr-sq ft-deg F | 0.0011
Sum zone sleeve metal and contact resistance |  | 0.0013726 |  | 0
Sum zone resistances, hr-sq ft deg F/Btu** |  | 0.012563 |  | 0.00236
Zone Us, Btu/hr-sq ft deg F 1/ sum zone resistance |  | 79.6012 |  | 423.7288
Restored duty, Btu/hr zone Us x zone surf. X LMTD |  | 1740978.78 | 9188164.7525 | 1149705.9322
Total restored duty increase, Btu/hr | 12078849.4647 | Sum of restored zone duties
Total duty decrement w sleeved tubes, Btu/hr | -213558.7535 | Restored duty - no plug duty
Total duty with sleeves, Btu/hr | 238076441.2465 | Sum no plug duty + decrement
Calc. FW out temp, deg. F (Sp. Ht. calc. basis) | 413.2588 | Sleeved duty/(FW flow x Sp. Ht.)+Inlet FW temp.
TTD with 100 full sleeved tubes, deg F | -1.9588 | Stm. Inlet sat. temp - sleeved FW out temp.
DCA w 100 sleeved tubes, deg F | 10.5156 | DCA +(drns out - FW in)/(rest./original duties)
**Note: Usually only the DSH is sleeved.
If the DC tubes are sleeved
insert the same number of sleeved tubes
for the DC as for the DSH.