## Sheet1
Company |  | Date
Job No. | Specimen Calculation
#No. of Passes to be Sleeved | 1
Fill in *Data from Mfr's. Data Sheet to Change from Example
*Number of U tubes | 1941 | From Mfr's. data sheet
*Estimated Average U-bend Length, In. | 13.6 | From U-tube schedule
*Total Est'd Straight Length, in. | 774 | Include lngth in tbsht
*Estimated Average Total Tube Length, In. | 787.6 | U-bend + straight lengths
*Data Sheet Tube Side Pressure Drop, psi | 16.3 | From Mfr's. data sheet
*OD of Tubes | 0.625 | From Mfr's. data sheet
*Wall thickness, in. | 0.057 | From Mfr's. data sheet
ID of Tubes, in. | 0.511 | Tube OD - 2 x tube wall
Flow Area/Tube, Sq. in. | 0.20508 | (Pi/4) x square of tube ID
Total Tube Flow Area, Asubt, Sq. in. | 398.068 | Inside flow area x No. of tubes
No. of Tubes to be Sleeved in One Pass | 100 | Sleeving plugged tubes
*Sleeve Length, in. | 774 | Length of sleeve
*Sleeve Thickness, in. | 0.01 | Thickness of sleeve
Sleeve ID, in. | 0.491 | Sleeve OD - 2 x sleeve wall
Flow Area/Sleeve, sq. in., Asubs | 0.18934 | (Pi/4) x square of Sleeve ID
Total Sleeve Flow Area, Asubt sq. in. | 18.9345 | Inside flow area x No. of sleeves
Flow Area Reduction Due to Sleeving, sq. in. | 1.5739 | No. to be sleeved x area diff.
*Flow Quantity, lb/h, W | 4939829 | From Mfr's. data sheet
Feedwater Inlet Temperature, Deg F | 367.3 | From Mfr's. data sheet
Feedwater Outlet Temperature, Deg F | 413.3 | From Mfr's. data sheet
Average FW Temp. in Sleeved leg, Deg F | 401.8 | 0.75 x outlet + 0.25 x inlet temps
**Density Correction Factor, C, Fig. 3a, HEI CFS | 0.86 | From HEI chart
Ksubt, Fig. 3b HEI CFS | 1.6 | From dwg and HEI figure
Exit/Entrance Delta P After Sleeving | 0.41816 | HEI calc.
Exit/Entrance Delta P Drop Before Sleeving | 0.41486 | HEI calc.
Increase Due to Entrance/Exit, psi | 0.0033002 | Before - after delta P
Delta P in Str. Lngths, Before Sleeving, psi | 15.8851 | Total delta P - ent/exit delta P
Delta P in Str. Lngths, After Sleeving, psi | 16.8137
Total Delta P After Sleeving, psi | 16.817 | Sum sleeved + ent/exit delta Ps
Increase in Delta P Due to Sleeving, psi | 0.93189 | Sum straight plus exit/ent delta P
#For full length sleeving only 1 if inlet pass
only, 2 if inlet and outlet pass are sleeved
*Values to change for new calculation
**Use inlet temperature for short sleeves,
average outlet leg temperature for full length sleeves.